{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":52,"n_cols":12,"rows_kept":52,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","EWWH-J-SS"]
[]
[]
[]
[]
["","","","","","EWWH090J-SS","EWWH110J-SS","EWWH120J-SS","EWWH130J-SS","EWWH150J-SS","EWWH180J-SS","EWWH200J-SS"]
["Aušinimo galingumas","Nom.","","","kW","88.77","107.1","115.1","133.5","150.1","181.6","200.6"]
["Galingumo valdymas","Būdas","","","","Belaipsnis","Belaipsnis","Belaipsnis","Belaipsnis","Belaipsnis","Belaipsnis","Belaipsnis"]
["","Minimalus galingumas","","","%","25","25","25","25","25","25","25"]
["Tiekiama galia","Aušinimas","","Nom.","kW","30","36.3","41.7","47.8","54.2","65.7","74.4"]
["EER","","","","","3.85","3.75","3.72","3.78","3.82","3.67","3.66"]
["IPLV","","","","","4.1","4.11","4.09","4.11","4.12","4.64","4.59"]
["SEER","","","","","3.36","3.38","3.32","3.4","3.39","3.87","3.82"]
["Matmenys","Įrenginys","","Gylis","mm","2684","2684","2684","2684","2684","2684","2684"]
["","","","Aukštis","mm","1020","1020","1020","1020","1020","1020","1020"]
["","","","Plotis","mm","913","913","913","913","913","913","913"]
["Svoris","Darbinis svoris","","","kg","1211","1276","1378","1415","1473","1663","1675"]
["","Įrenginys","","","kg","1177","1233","1334","1366","1416","1600","1607"]
["Korpusas","Spalva","","","","Dramblio kaulo balta spalva","Dramblio kaulo balta spalva","Dramblio kaulo balta spalva","Dramblio kaulo balta spalva","Dramblio kaulo balta spalva","Dramblio kaulo balta spalva","Dramblio kaulo balta spalva"]
["","Medžiaga","","","","Galvanizuotas plienas","Galvanizuotas plienas","Galvanizuotas plienas","Galvanizuotas plienas","Galvanizuotas plienas","Galvanizuotas plienas","Galvanizuotas plienas"]
["Vandens šilumokaitis – garintuvas","Tipas","","","","Plokštelinis šilumokaitis","Plokštelinis šilumokaitis","Plokštelinis šilumokaitis","Plokštelinis šilumokaitis","Plokštelinis šilumokaitis","Plokštelinis šilumokaitis","Plokštelinis šilumokaitis"]
["","Vandens tūris","","","l","14","18","14","17","20","26","26"]
["Vandens šilumokaitis – garinis","Vandens slėgio kritimas","Vėsinimas","Nom.","kPa","10.7","10.9","19.3","19.3","17.8","16.8","20.1"]
["Kompresorius","Kiekis_","","","","1","1","1","1","1","1","1"]
["","Tipas","","","","Viensraigtis kompresorius","Viensraigtis kompresorius","Viensraigtis kompresorius","Viensraigtis kompresorius","Viensraigtis kompresorius","Viensraigtis kompresorius","Viensraigtis kompresorius"]
["","Paleidimo metodas_","","","","Wye-Delta","Wye-Delta","Wye-Delta","Wye-Delta","Wye-Delta","Wye-Delta","Wye-Delta"]
["Darbo diapazonas","Vandens pusė","Garintuvas","Min.","° CDB","-5","-5","-5","-5","-5","-5","-5"]
["","","","Maks.","° CDB","25","25","25","25","25","25","25"]
["Garso galingumo lygis","Aušinimas","","Nom.","dBA","95","95","95","95","95","95","95"]
["Garso slėgio lygis","Aušinimas","","Nom.","dBA","79","79","79","79","79","79","79"]
["Šaltnešis","Tipas","","","","R-1234(ze)","R-1234(ze)","R-1234(ze)","R-1234(ze)","R-1234(ze)","R-1234(ze)","R-1234(ze)"]
["Aušinimo medžiaga","GWP","","","","1.4","1.4","1.4","1.4","1.4","1.4","1.4"]
["","Užpildytas kiekis","","","kg","18","35","34","37","37","38","38"]
["Šaltnešis","Grandinės","","Kiekis","","1","1","1","1","1","1","1"]
["Vamzdžių jungtys","Garintuvo vandens įleidimo ir išleidimo vamzdis (OD)","","","","76.2 mm","76.2 mm","76.2 mm","76.2 mm","76.2 mm","76.2 mm","76.2 mm"]
["Energijos naudojimo efektyvumo klasė","","","","","Space Heating A+++ ~ D, Water Heating A+ ~ F","Space Heating A+++ ~ D, Water Heating A+ ~ F","Space Heating A+++ ~ D, Water Heating A+ ~ F","Space Heating A+++ ~ D, Water Heating A+ ~ F","Space Heating A+++ ~ D, Water Heating A+ ~ F","Space Heating A+++ ~ D, Water Heating A+ ~ F","Space Heating A+++ ~ D, Water Heating A+ ~ F"]
["El. tiekimas","Fazė","","","","3~","3~","3~","3~","3~","3~","3~"]
["Maitinimas","Dažnis","","","Hz","50","50","50","50","50","50","50"]
["","Įtampa","","","V","400","400","400","400","400","400","400"]
["","Įtampos intervalas","","Min.","%","-10","-10","-10","-10","-10","-10","-10"]
["","","","Maks.","%","10","10","10","10","10","10","10"]
["Įreng.","Paleid. srovė","","Maks.","A","153","153","197","197","197","290","290"]
["","Darb. srovė","Vėsinimas","Nom.","A","39","44","55","60","65","76","84"]
["","","","Maks.","A","75","90","100","114","143","158","178"]
["Vienetas","Maksimali įrenginio srovė laidų dydžiams","","","A","83","100","112","127","159","176","198"]
["Pastabos","","","","","(1) - Vėsinimas: EW 12 °C; LW 7 °C; aplinkos sąlygos: 35 °C DB","(1) - Vėsinimas: EW 12 °C; LW 7 °C; aplinkos sąlygos: 35 °C DB","(1) - Vėsinimas: EW 12 °C; LW 7 °C; aplinkos sąlygos: 35 °C DB","(1) - Vėsinimas: EW 12 °C; LW 7 °C; aplinkos sąlygos: 35 °C DB","(1) - Vėsinimas: EW 12 °C; LW 7 °C; aplinkos sąlygos: 35 °C DB","(1) - Vėsinimas: EW 12 °C; LW 7 °C; aplinkos sąlygos: 35 °C DB","(1) - Vėsinimas: EW 12 °C; LW 7 °C; aplinkos sąlygos: 35 °C DB"]
["","","","","","(2) - Vėsinimas: EW 23 °C; LW 18 °C; aplinkos sąlygos: 35 °C DB","(2) - Vėsinimas: EW 23 °C; LW 18 °C; aplinkos sąlygos: 35 °C DB","(2) - Vėsinimas: EW 23 °C; LW 18 °C; aplinkos sąlygos: 35 °C DB","(2) - Vėsinimas: EW 23 °C; LW 18 °C; aplinkos sąlygos: 35 °C DB","(2) - Vėsinimas: EW 23 °C; LW 18 °C; aplinkos sąlygos: 35 °C DB","(2) - Vėsinimas: EW 23 °C; LW 18 °C; aplinkos sąlygos: 35 °C DB","(2) - Vėsinimas: EW 23 °C; LW 18 °C; aplinkos sąlygos: 35 °C DB"]
["","","","","","(3) - Sąlyga: Ta DB/WB 7 °C/6 °C - LWC 35 °C (DT = 5 °C)","(3) - Sąlyga: Ta DB/WB 7 °C/6 °C - LWC 35 °C (DT = 5 °C)","(3) - Sąlyga: Ta DB/WB 7 °C/6 °C - LWC 35 °C (DT = 5 °C)","(3) - Sąlyga: Ta DB/WB 7 °C/6 °C - LWC 35 °C (DT = 5 °C)","(3) - Sąlyga: Ta DB/WB 7 °C/6 °C - LWC 35 °C (DT = 5 °C)","(3) - Sąlyga: Ta DB/WB 7 °C/6 °C - LWC 35 °C (DT = 5 °C)","(3) - Sąlyga: Ta DB/WB 7 °C/6 °C - LWC 35 °C (DT = 5 °C)"]
["","","","","","(4) - Sąlyga: Ta DB/WB 7 °C/6 °C - LWC 45 °C (Dt=5 °C)","(4) - Sąlyga: Ta DB/WB 7 °C/6 °C - LWC 45 °C (Dt=5 °C)","(4) - Sąlyga: Ta DB/WB 7 °C/6 °C - LWC 45 °C (Dt=5 °C)","(4) - Sąlyga: Ta DB/WB 7 °C/6 °C - LWC 45 °C (Dt=5 °C)","(4) - Sąlyga: Ta DB/WB 7 °C/6 °C - LWC 45 °C (Dt=5 °C)","(4) - Sąlyga: Ta DB/WB 7 °C/6 °C - LWC 45 °C (Dt=5 °C)","(4) - Sąlyga: Ta DB/WB 7 °C/6 °C - LWC 45 °C (Dt=5 °C)"]
["","","","","","(5) - Pagal EN14825","(5) - Pagal EN14825","(5) - Pagal EN14825","(5) - Pagal EN14825","(5) - Pagal EN14825","(5) - Pagal EN14825","(5) - Pagal EN14825"]
["","","","","","(6) - Priklauso nuo darbinio režimo, žr. įrengimo vadovą.","(6) - Priklauso nuo darbinio režimo, žr. įrengimo vadovą.","(6) - Priklauso nuo darbinio režimo, žr. įrengimo vadovą.","(6) - Priklauso nuo darbinio režimo, žr. įrengimo vadovą.","(6) - Priklauso nuo darbinio režimo, žr. įrengimo vadovą.","(6) - Priklauso nuo darbinio režimo, žr. įrengimo vadovą.","(6) - Priklauso nuo darbinio režimo, žr. įrengimo vadovą."]
["","","","","","(7) - Daugiau informacijos rasite veikimo diapazono brėžinyje","(7) - Daugiau informacijos rasite veikimo diapazono brėžinyje","(7) - Daugiau informacijos rasite veikimo diapazono brėžinyje","(7) - Daugiau informacijos rasite veikimo diapazono brėžinyje","(7) - Daugiau informacijos rasite veikimo diapazono brėžinyje","(7) - Daugiau informacijos rasite veikimo diapazono brėžinyje","(7) - Daugiau informacijos rasite veikimo diapazono brėžinyje"]